## Slide 1: Industrial Automation OPC

## Slide 2
OLE for Process Control (OPC)

## Slide 3
OPC Overview
OPC Common
OPC Data Access
OPC Alarms and Events Specification
OPC Historical Data Specification
Applications

## Slide 4
Executive Summary
OPC is a set of standard commands collected in a software library (DLL) that can be called by client applications, written in Visual Basic, C# or other Microsoft programming languages, that allow to access automation devices (PLCs) in a uniform way, independently from their built or manufacturer.
To that effect, the particularities of the automation devices are hidden by an OPC server running either on the same machine as the client program or on another machine, by using DCOM. The OPC Servers are supplied by the manufacturer of the PLC or by 3rd parties and can manage several PLCs of the same type. Several servers can run in parallel.
The OPC library allows in particular to read and write process variables, read alarms and events and acknowledge alarms, and retrieve historical data from data bases according to several criteria.
Automation platforms such as ABB's 800XA platform act as OPC clients to collect data from PLCs or databases through third-party OPC servers. Several automation platforms act themselves as an OPC server to publish their data, events and historical data.
OPC is the preferred connectivity for 78% of MES, 75% of HMI / SCADA, 68% of DCS / PLC and 53% or ERP /Enterprise system level applications (according to Arc Advisory Group, 2004)"

## Slide 5
Where is OPC in a system?
Experimental equipment
. . .
LAN
WAN
Storage
Other systems
(LHC, Safety, ...)
Configuration DB,
Archives,
Logfiles, etc.
Controller/
PLC
VME
FieldBus
LAN
Supervision
Process
Management
Field
Management
Sensors/devices
Field buses
PLC
OPC
Communication
Protocols
SCADA
Technologies
SCADA = supervisory control and data acquisition
OPC = OLE for process control
PLC = Programmable logic controller
Field buses = CAN, ProfiBus, WorldFip, ...

## Slide 6
What is OPC ?
OPC (formerly: "OLE1 for Process Control", now: "Open Process Control") is
an industry standard set up by the OPC Foundation specifying the software interface (objects, methods) to a server that collects data produced by field devices and programmable logic controllers.
OPC server X
application
(OPC client)
OPC server
(simulator)
OPC server
Y
interfaces covered by the OPC standard
node
servers
PLCs Brand X
PLCs Brand Y
Field bus (not covered)
Ethernet (not covered)
Sensors/Actors
1) OLE (Object Linking and Embedding) is a Microsoft technology for connecting software components.
It has since been extended by the COM / DCOM technology. It corresponds to Java Beans.

## Slide 7
Before OPC
ABB PLCs
Télémécanique PLCs
Siemens PLCs
MasterBus
MMS driver
XWAY
driver
Profinet
driver
visualization
history
data base

## Slide 8
With OPC: ABB Operator Workplace Connection
ABB AC800M
Télémécanique TSX
Siemens S7
AC800M OPC server
Schneider OPC server
Siemens OPC server
OperatorIT
application software is written independently from the type of controller
Historian
(Information Manager)
MMS
XWAY
ProfiNet
the drivers still exist,
but the clients do not
see them anymore

## Slide 9
The main OPC Specifications
OPC
Data Access
OPC Alarms & Events
OPC HDA
history
data base
OPC Batch
batch
system
OPC DX
OPC UA

## Slide 10
Specification 1: OPC DA for Data Access
Process variables describe the plant's state, they are generated by the sensors or calculated in the programmable logic controllers (PLCs).
Process variables can be sent upon a change, on demand or when a given time elapsed.
The OPC DA (Data Access) specification addresses collecting Process Variables. The main clients of OPC DA are visualization and (soft-) control.

## Slide 11
Specification 2: OPC AE for Alarms and Events
determine the exact time of change (time stamping)
categorize by priorities
log for further use
acknowledge alarms (events are not acknowledged)
link to clear text explanation
Events are changes in the process that need to be logged, such as "production start"
Alarms are abnormal states in the process that require attention, such as "low oil pressure"
OPC AE (Alarms and Events) specifies how alarms and events are subscribed, under which conditions they are filtered and sent with their associated messages. The main clients of OPC AE are the Alarms and Event loggers.

## Slide 12
Specification 3: HDA for Historical Data Access
Historical Data are process states and events such as: process variables, operator actions, recorded alarms,... that are stored as logs in a long-term storage for later analysis.
OPC HDA (Historical Data Access) specifies how historical data are retrieved from the logs in the long-term storage, filtered and aggregated (e.g. compute averages, peaks).

## Slide 13
Specification 4: OPC Batch
based on:
IEC 61512-1 Batch Control – Part 1: Models and Terminology
(ANSI/ISA S88.01 1995)
ISA-dS88.02-2000 draft 17 of May 2000
allows to access:
equipment capabilities,
current operating conditions,
historical and
recipe contents

## Slide 14
Beyond Microsoft: OPC UA
In a move to get more independence from Microsoft and use web technology,
a new specification called " Unified Architecture" (formerly. OPC XML) that uses web services for all kinds of transactions: query, read, write, subscribe,...
The classical OPC DA, AE and HDA are implemented with XML / SOAP /WSDL
this allows encryption and authentication of process data.
This does not only standardize the interfaces, but also the transmitted data.

## Slide 15
OPC as a hub
OPC variables is also a convenient way to exchange data between applications
on the same machine. OPC data can be easily read in any Microsoft Office application
source: Siemens WinCC

## Slide 16
OPC connection to databases
Tools such as LifeWire’s allow to build an OPC DA interface to any ODBC - equipped database.
The database internal structure (exposed through queries) is reflected as a hierarchy of OPC items.
This allows to give a unified access to simple items.
application
(OPC client)
OPC server
DB
ODBC

## Slide 17
Server(s) and Client(s) in the same node
OPC server
client application
(OPC client)
OPC server
OPC server
client application
(OPC client)
Clients and servers run as parallel processes
The OPC specification defines the interface between client and server in the form
of objects and methods.
devices
devices
devices
devices
node

## Slide 18
Direct and Fieldbus access
(local)
OPC server
client application
(OPC client)
fieldbus
(local)
OPC server
FB Manager
fieldbus
PLC
FB agent
fieldbus
PLC
FB agent
direct connection
fieldbus connection
can also be a point-to-point link
client application
(OPC client)
proprietary protocol
The OPC server is running
all the time, as soon as at
least one client is present
I/O devices
clients and servers run as parallel processes

## Slide 19
Full-fledged COM/DCOM across multiple nodes
OPC server
for BrandY
application 1
(OPC client)
Fieldbus Y
Fieldbus X
drivers
OPC server
for BrandX
OPC server
for simulation
panel
application 2
(OPC client)
The OPC servers supports multiple clients and servers on the same, or on remote nodes. They run as separate processes (as soon as at least one client is requesting them)
OPC server
for BrandZ
TCP/IP
TCP/IP
input / output to plant
Ethernet
app3
node 1
connectivity node

## Slide 20
OPC technologies
Transport
(TCP-IP, UDP, Queued)
ActiveX
(Distributed) Component Object Model
(COM / DCOM)
Object Linking and
Embedding (OLE)
Ethernet
OLE for Process
Control (OPC)
OPC bases on Microsoft's COM/DCOM technology (i.e. it only works on Windows platforms).
Effort to port it to other platforms (Linux) and web transport protocols (XML) are in progress. Advantages are the direct integration into all applications, such as Excel.
only between
nodes

## Slide 21
Structure of an OPC server
OPC/COM Interfaces
OPC Group & Item Management
Item Data Optimization and Monitoring
Device Specific Protocol Logic
Hardware Connection Management

## Slide 22
OPC Overview
OPC Common
OPC Data Access
OPC Alarms and Events Specification
OPC Historical Data Specification
Applications

## Slide 23
OPC DA: Scope of specification
controller
OPC DA Client e.g. visualization
OPC DA Server
e.g. Ethernet
controllers
field devices
OPC DA Client e.g. performance indicator
OPC DA specified interface
plant measurement points
An OPC DA Server
is configured using the information coming from the
development tools for the controllers
tags
Variables defined in the controllers are mirrored to the OPC DA server
controller
field bus

## Slide 24
OPC DA: Example of access to a variable
Network
controller development
OPC
server
Reactor_1
Oven controller
analog input to : IXD.11.2.1
MW%1003
MotorSpeed
MW%1004
Temperature
…
….
symbols
load
symbol
table
ReadItem ("OPC:Reactor1: Program2.MotorSpeed")
Get (192.162.0.2), MW%1003)
Return (MW%1003, 112)
Value: 112
Reactor_1.Program2
Program 2
code
Marker: MW%1003
OPC application

## Slide 25
OPC DA: Objects as viewed by the OPC server
An OPC server is structured as a directory with root, branches and leaves (items)
Controller 1
Machine 2
Controller 2
Controller_3.Prog_2
Controller_3.Prog_1
Cell 1
Level_1
Level_2
Ramp4
TAG
TAG
TAG
Branches may contain other branches and items
The structure may also be flat instead of hierarchical
This structure is defined during engineering of the attached devices and sensor/actors.
(Intelligent servers could configure themselves by reading the attached devices)
An item is identified by its "fully qualified ItemID", e.g.
"Process_Line_1.Controller_2.Level_2"
Process Line 1
the hierarchical position may differ from
the fully qualified ItemID
this will be detailed under „browsing“
Tag Name

## Slide 26
OPC DA: Objects as viewed by the OPC client
Each client structures its items by groups, independently from the server.
Initially, the client browses the server structure to check if the items it is interested in exist.
A client registers its groups and items at the server. The server keeps the structure of all its clients.
Temperature
Heat_On
TAG
TAG
Server root
GroupX
Level
Empty_Valve
Fill_Valve
TAG
TAG
TAG
Area 1
Area 51
Oven_1
Tank_1
Area 2
GroupZ
Client1
Item1
Item2
Item3
Item1
Item2
server
clients
Client2

## Slide 27
OPC DA: Item properties
The process data are represented by three dynamic properties of an item:
value: numerical or text
time-stamp: the time at which this data was transmitted from the PLC to the server
this time is UTC (Greenwich Winter time), not local time.
quality: validity of the reading (not readable, dubious data, o.k.)
(when writing, only the value is used)

## Slide 28
OPC DA: Item types
Boolean,
Character,
Byte, (1 byte)
Word, (2 bytes)
Double Word, (4 bytes)
Short Integer (2 bytes)
Integer (4 bytes)
Long Integer:
Long Unsigned Integer
Single Float (4 bytes)
Double Float (8 bytes)
Currency,
Date,
String,
Array of "the above"
Each item value has a type:
When accessing an item, the client may request
that it is returned with a specific type, which could
be different from the server's type.
(The server's type is returned by browsing)
Type conversion is left to the server, there are no rules
whether and how a server does the conversion.
(use with caution)
Care must be taken that the data types in the
programming language or in the database match those
of the OPC Server.
Items also may have engineering units, but this option is not often used.

## Slide 29
OPC DA: Program - initialising a connection
find out existing OPC servers
connect to that OPC server
create an OPCBrowser object
create an OPCGroups object
create an OPCServer object
create an OPCGroup object
build array of items checking with the browser that these items exist in this server
add item array to the group
activate and subscribe group
myDummyServer.GetOPCServers
myServer.Connect
Set myBrowser = myServer.Browser
Set myGroups = myServer.Groups
myServer = new OPCServer
Set myGroup1 = myGroups.Add Set MyItems = MyGroup1.OPCItems
FQItems1[1] = "Device1.Temp1"
ClientHandle1[1] = 101
ReDim ServerHandle1(nrItems)
ReDim ServerErrors1(nrItems)
ReDim Value1(nrItems)
myGroup1.AddItems
myGroup1.IsActive
myGroup1.IsSubscribed
next
group

## Slide 30
OPC DA: Libraries
The OPC DA specification is not formal, conformance can hardly be checked against this document.
To ensure that the standard is observed, the OPC foundation distributes on its website
the DLLs (opcdaauto.dll, opccomn_ps,…) that contain the type libraries to access the
OPC server.
The vendors are not compelled to implement all features. For instance, the description of the variables is seldom used. Calling unimplemented functions causes exceptions that must be caught in Visual Basic with "On Error …" statements.
There exist three versions of DA, 1.0, 2.0 and 3.0, that behave differently, however, older servers do not have a property indicating which version they support.

## Slide 31
OPC DA: Custom Interface
OPC
group
IOPCItemMgt
IOPCGroupStateMgt
[IOPCPublicGroupSteatMgt]
IOPCSyncIO
IOPCAsyncIO2
IConnectionPointContainer
IEnumOPCItemAttributes
IOPCSyncIO
IDataObject
OPC
client
IOPCDataCallback
IOPCServerShutdown
OPC
server
IOPCCommon
IOPCServer
IConnectionPointContainer
IOPCItemProperties
[IOPCServerPublicGroups]
IConnectionPointContainer
[IOPCBrowseServerAddressSpace]
IPersistFile
While the Automation Interface is easy to use and quite powerful, some OPC functions are missing and special operations can only be done in Visual C++ using the custom COM interface.
This is only recommended for experienced programmers.

## Slide 32
OPC Overview
OPC Common
OPC Data Access
OPC Alarms and Events Specification
OPC Historical Data Specification
Applications

## Slide 33
OPC AE: Configuration
controller
OPC AE Client e.g. event logger
OPC AE Server
e.g. Ethernet
controllers
field devices
OPC AE Client e.g. alarm printer
OPC A&E specified interface
plant measurement points
event notification
An OPC AE Server
is configured using the information coming from the
development tools for the controllers
events
Events defined in the controllers are mirrored to the OPC AE server
controller
field bus

## Slide 34
OPC AE: Purpose
The controllers (PLC) generate events in response to changes in the plant variables.
together with their precise time of occurrence, type, severity and associated message for the human operator.
An OPC Event server registers these events and makes them available to several clients
A particular class of events are the alarms, which are detailed events that may require
acknowledgement.
The OPC Alarms & Events Interface gives access to the OPC Event server, allowing to:
- browse the OPC A&E Server for predefined events.
- enable or disable alarms and events
- subscribe to alarms and events of interest
- receive the event and alarm notifications with the associated attributes
- acknowledge alarms

## Slide 35
OPC AE: Displaying Alarms and Events
Alarms and events are usually displayed differently on an operator screen.
- Events are displayed in an event list that can become quite long (typically 1000 entries), entries are not cleared when the source of the event returns to normal
- Alarms are displayed in a short list (typically 50 alarms) appearance changes when the alarm is acknowledged, an alarm line is cleared when the alarm signal is cleared.
Ack checkbox

## Slide 36
OPC AE: Summary alarms and events
controller
OPC AE Server
AE Client
Condition
OPC AE Server
timestamp
AE Client
event notification (source, timestamp, message)
message
message
alarm notification (source, timestamp, message, condition, subcondition, severity, type)
Event FB
controller
Event
Alarm

## Slide 37
OPC Overview
OPC Common
OPC Data Access
OPC Alarms and Events Specification
OPC Historical Data Specification
Applications

## Slide 38
OPC HDA: Historical Data Access
Field device
OPC HDA Server
HDA Clients
independent processes
history
database
Field device
OPC DA Server
proprietary data acquisition
e.g. Event Logger
e.g. Trend Analysis
calculations
collector
raw and ordered data
hidden

## Slide 39
OPC HDA: Purpose
An OPC HDA server gives access to a historical data base (logs) in which data from the process have been collected and time-stamped, possibly through an OPC DA interface.
The OPC HDA interface clients, such as trend analysis, product tracking or data mining,
that require ordered access these data logs.
The OPC HDA interface allows to:
- browse the historical data base
- retrieve data through proper filtering, e.g. by date range, by identity, by property
- build aggregates over the retrieved data, such as average, minimum, maximum.
- enter new entries, correct entries or remove entries
- enter / delete annotations in the history data base

## Slide 40
OPC HDA: Application
Parameters:
time scale (with possible offset, zoom, pan)
amplitude scale (low range, high range, scale units)
style: smoothed, stepped, filled (several ways to display the same data)
extrapolate: how to display values not received (e.g. because they did not yet change)
log: how were
data sampled

## Slide 41
OPC HDA: Automation Interface summary
An collection containing a series of either OPCHDAValue or OPCHDAEntry objects, representing historical values of an item.
OPCHDABrowsers
OPCHDAServer
OPCHDAItems (col)
OPCHDAItem
OPCHDAItem
OPCHDAValue
OPCHDAEntry
An instance of an OPC HDA Server. An OPCHDAServer object must be created to can get references to other objects.
A collection containing all the OPCHDAItem objects this client has created within the scope of the OPCHDAServer object
An object that maintains the item’s definition. Note the Custom Interface does not provide a separate Item Object.
An object that browses item names in the server’s configuration.
OPCHDAValue
An object that extends the OPCHDAValue object to include additional information
An object that represents a discrete historical value for an item or an attribute.
OPCHDAEntry
OPCHDAHistory

## Slide 42
OPC Overview
OPC Common
OPC Data Access
OPC Alarms and Events Specification
OPC Historical Data Specification
Applications

## Slide 43
Field protocols: 101, 61850, HTTP
Applications: OPC & SCADA
Data Acquisition
Process data
base
Historian
Reporting &
Logging
Measurand
processing
Command
language &
procedures
OPC DA
Application
functions
ActiveX
Remote Device
Configuration
Communication
stream
ODBC/SQL
History data base
FDT / DTM / XML
Alarm & Event
handling
OPC AE
HMI
standards

## Slide 44
Model-Viewer-Controller
web-pages
(HTM, JSP, ASP,..)
data base
page logic
code-behind
(servlets, .NET
web server
(IIS, TomCat)
scripts & code
(Java, Perl, C#,..)
browser
on same or other machine
(IE, Netscape,…)
Applications: OPC & SCADA